Non-metallic Casing Spacer & End Seal
Typical Specification (Water Market) for Carrier Pipe up to 37.60 O.D.

A. Casing Spacers
Upon completion of the installation of the steel pipe encasement, the contractor shall furnish and install a Ranger II® boltless casing spacer on the carrier pipe as described below.
Casing spacers shall be spaced a maximum of eight (8) feet apart along the length of the carrier pipe with one casing spacer within two (2) feet of each side of a pipe joint and the rest evenly spaced. Wood skids are not an acceptable method of supporting the carrier pipe.

1. Casing spacers shall be all non-metallic (polypropylene), molded in segments for field assembly without any special tools. Spacer segments shall be secured around carrier pipe by insertion of a Slide-Lock. The casing spacer polymer shall contain ultraviolet inhibitors and shall have a minimum compressive strength of 3,000 psi, an 800 Volts/mil dielectric strength and impact strength of 1.5 ft-lbs./inch. Each casing spacer shall have full length, integrally molded skids extending beyond the bell or mechanical joint of the carrier pipe.
2. The casing spacers shall be the PSI Ranger II® Casing Spacers as manufactured by PSI / Pikotek, Houston, Texas. Casing Spacers shall be purchased through authorized stocking distributor MDG Equipment Co., Inc., Phoenixville, PA (Tel: 610-935-9500) or equal with at least 10 years of service.

3. Spacers shall be at least as wide as listed below.

| Carrier Pipe Diameter Inches (mm) | Ranger II Model | Length Inches (mm) |
| --- | --- | --- |
| 0.83 to 3.07" (21 to 78) | Micro | 2.13" (54) |
| 2.48 to 5.51" (63 to 140) | Mini | 3.15" (80) |
| 5.51 to 16.65" (140 to 423) | Midi | 5.12" (130) |
| 16.77 to 25.98" (426 to 660) | Medi | 6.87" (174) |
| 25.98 to 37.60" (660 to 955) | Maxi | 8.86" (225) |

B. End Seals
After insertion of the carrier pipe into the casing, the ends of the casing shall be closed by installing 1/8" thick synthetic rubber end seals equal to the PSI Model "C" end seal as manufactured by PSI / Pikotek, Houston, Texas. End Seals shall be purchased through authorized stocking distributor MDG Equipment Co., Inc., Phoenixville, PA (Tel: 610-935-9500) or equal with at least 10 years of service.

ISO 9001:2008 Registration
Each casing spacer and end seal shall be manufactured at a facility that has a Registered ISO 9001:2008 Quality Management System. Copy of current ISO 9001:2000 Registration shall be provided with material submittal.